## Sheet1
Sodium hypochlorite strength (%) | Volume to chlorinate (m3) | Volume (litres) | Chlorine dose (mg/l) | Sodium hypochlorite volume needed (litres) | Sodium hypochlorite volume needed (ml) | Dosatron % Flow rate to achieve 50 mg/l
2 | 0.628 | 628 | 50 | 1.57 | 1570 | 0.25
Tank volume calculation
Depth of water (m) | 0.9
Width of tank (m) | 2
Length of tank (m) | 3
Total volume of tank (m3) | 5.4
MDPE pipe
Pipe external diameter (mm) | Pipe internal diameter (mm) | Pipe internal diameter (cm) | Litres/metre
20 | 15.2 | 1.52 | 0.18137
25 | 20.1 | 2.01 | 0.31715
32 | 25.8 | 2.58 | 0.52253
50 | 40.4 | 4.04 | 1.2812
63 | 50.9 | 5.09 | 2.0338
Copper pipe
15 | 13.6 | 1.36 | 0.14519
22 | 20.2 | 2.02 | 0.32031
28 | 26.2 | 2.62 | 0.53886
Custom pipe size capacity
Internal diameter (mm) | 100
Length (m) | 80
Volume (m3) | 0.628
Volume (litres) | 628
Only change numbers in grey cells, numbers in yellow cells are calculated
The above calulation assumes a direct relationship between sodium hypochlorite added and chlorine residual however in practice this is unlikely as chlorine will dissipate through storage and demand in water. The calculation also does not take into account the specific gravity of sodium hypochlorite solution. Sodium hypochlorite has an S.G. of 1.2 which depending on how the sodium hypochlorite is sold (either vol/vol or weight/vol), will effect the dose rate. More sodium hypochlorite than calculated will need to be added to acheive the desired chlorine residual.
Sodium hypochlorite strength is typical 10-11% or 14-15% as supplied. A 1 in 10 dilution will normally be needed to achieve dosing in target range using a dosatron.